## Dry Installed Pump
NPSH Calculation
Input Data |  | Calculation
Max Temperature (°C) | 10 | Water Density (Kg/m3) | 999.6853
Altitude Above Sea Level (m) | 0 | Vapor Pressure (Pvapor) (105 Pa) | 0.012317
Pump reference inlet Level (m) | 10 | Atm. Pressure (Patm) (kPa) | 101.2508
Water surface level (m) | 5 | S (Hgeo ) (m) | -5
Suction line head loss (m) | 0.3 | Hatm (m) | 10.3244
NPSHr (m) | 2.21 | Hl (m) | 0.3
Data accuracy relevant margin (m) | 1 | Hvapor (m) | 0.1256
|  | NPSHa (m) | 4.8988 | NPSHa>NPSHr
|  | Available Margin (m) | 2.6888 | OK
Note: - Results have been calculated for water medium. For other mediums density and vapor pressure would vary accordingly. - NPSHr would be recommended by pump manufaturer based on performed pump test according to ISO 9906. - Relevant margin has to be decided from case to case and would be dependednt on the accuracy of inputed data. (Less accuracy = Higher margin) - Its user's responsibility to check or validate the right input data.
S (-)
Hatm
S
Hatm
Pump Inlet level
Pump Inlet level

## Submerged Installed Pump
NPSH Calculation
Input Data |  | Calculation
Max Temperature (°C) | 30 | Water Density (Kg/m3) | 995.7076
Altitude Above Sea Level (m) | 500 | Vapor Pressure (Pvapor) (105 Pa) | 0.042383
Pump reference inlet Level (m) | 5 | Atm. Pressure (Patm) (kPa) | 95.4421
Water surface level (m) | 10 | S (Hgeo ) (m) | 5
Suction side head loss (m) | 0.64 | Hatm (m) | 9.771
NPSHr (m) | 9 | Hl (m) | 0.64
Data accuracy relevant margin (m) | 5 | Hvapor (m) | 0.4339
|  | NPSHa (m) | 13.6971 | NPSHa>NPSHr
|  | Available Margin (m) | 4.6971 | Not OK
Note: - Results have been calculated for water medium. For other mediums density and vapor pressure would vary accordingly. - NPSHr would be recommended by pump manufaturer based on performed pump test according to ISO 9906. - Relevant margin has to be decided from case to case and would be dependednt on the accuracy of inputed data. (Less accuracy = Higher margin) - Its user's responsibility to check or validate the right input data.
S
Hatm
Hatm
S
Pump Inlet level
Pump Inlet level

## values (hidden)
| T | Vapor pressure | Density |  | Vapor pressure | Density
| 0 | 0.00611 | 1000 |  | 0.0060692 | 999.9926
| 4 | 0.00813 | 1000 |  | 0.0081647 | 1000.0187 |  | Barometric Pressure vs. Altitude
| 10 | 0.01227 | 999.7 |  | 0.012317 | 999.6853 |  | Altitude Above Sea Level |  | Temperature | Barometer |  | Atmospheric Pressure
| 20 | 0.02337 | 998.2 |  | 0.023356 | 998.2113 |  | Feet | Meters | C | In. Hg. Abs. | mm Hg. Abs. | PSI | Kg / cm2 | kPa
| 25 | 0.03166 | 997.1 |  | 0.031632 | 997.0799 |  | -5000 | -1526 | 25 | 35.58 | 903.7 | 17.48 | 1229 | 120.5 | 120.6673
| 30 | 0.04241 | 995.7 |  | 0.042383 | 995.7076 |  | -4500 | -1373 | 24 | 35.00 | 889.0 | 17.19 | 1209 | 118.5 | 118.602
| 40 | 0.07375 | 992.3 |  | 0.073741 | 992.3017 |  | -4000 | -1220 | 23 | 34.42 | 874.3 | 16.9 | 1188 | 116.5 | 116.5637
| 50 | 0.12335 | 988.1 |  | 0.12337 | 988.1084 |  | -3500 | -1068 | 22 | 33.84 | 859.5 | 16.62 | 1169 | 114.6 | 114.5652
| 60 | 0.1992 | 983.2 |  | 0.19923 | 983.2272 |  | -3000 | -915 | 21 | 33.27 | 845.1 | 16.34 | 1149 | 112.7 | 112.58
| 70 | 0.31162 | 977.8 |  | 0.31163 | 977.7411 |  | -2500 | -763 | 20 | 32.70 | 830.6 | 16.06 | 1129 | 110.7 | 110.6339
| 80 | 0.4736 | 971.7 |  | 0.47359 | 971.7154 |  | -2000 | -610 | 19 | 32.14 | 816.4 | 15.78 | 1109 | 108.8 | 108.7011
| 90 | 0.70109 | 965.2 |  | 0.70106 | 965.1987 |  | -1500 | -458 | 18 | 31.58 | 802.1 | 15.51 | 1091 | 106.9 | 106.8066
| 100 | 1.0132 | 958.2 |  | 1.0132 | 958.2239 |  | -1000 | -305 | 17 | 31.02 | 787.9 | 15.23 | 1071 | 105 | 104.9252
| 110 | 1.4327 | 950.8 |  | 1.4327 | 950.8107 |  | -500 | -153 | 16 | 30.47 | 773.9 | 14.96 | 1052 | 103.1 | 103.0814
| 120 | 1.9854 | 943 |  | 1.9855 | 942.9684 |  | 0 | 0 | 15 | 29.92 | 760.0 | 14696 | 10333 | 101.33 | 101.2508
| 130 | 2.7013 | 934.7 |  | 2.7013 | 934.7004 |  | 500 | 153 | 14 | 29.38 | 746.3 | 14.43 | 1015 | 99.49 | 99.4452
| 140 | 3.6138 | 926 |  | 3.6138 | 926.009 |  | 1000 | 305 | 13 | 28.86 | 733.0 | 14.16 | 0.996 | 97.63 | 97.6761
| 150 | 4.76 | 916.9 |  | 4.7599 | 916.9017 |  | 1500 | 458 | 12 | 28.33 | 719.6 | 13.91 | 0.978 | 95.91 | 95.9199
| 160 | 6.1806 | 907.4 |  | 6.1807 | 907.3979 |  | 2000 | 610 | 11 | 27.82 | 706.6 | 13.66 | 0.960 | 94.19 | 94.1995
[8 empty] | 2500 | 763 | 10 | 27.32 | 693.9 | 13.41 | 0.943 | 92.46 | 92.4919
[8 empty] | 3000 | 915 | 9 | 26.82 | 681.2 | 13.17 | 0.926 | 90.81 | 90.8193
[8 empty] | 3500 | 1068 | 8 | 26.33 | 668.8 | 12.93 | 0.909 | 89.15 | 89.1595
[8 empty] | 4000 | 1220 | 7 | 25.84 | 656.3 | 12.69 | 0.892 | 87.49 | 87.534
V-T |  |  | p-T |  |  | Atm pressure |  | 4500 | 1373 | 6 | 25.37 | 644.4 | 12.46 | 0.876 | 85.91 | 85.9211
C6 | -6.0044e-14 |  | C6 | 1.3036e-12 |  | C6 | -5.2344e-27 | 5000 | 1526 | 5 | 24.90 | 632.5 | 12.23 | 0.86 | 84.33 | 84.3314
C5 | 4.6498e-11 |  | C5 | -4.7711e-10 |  | C5 | 1.4878e-21 | 6000 | 1831 | 3 | 23.99 | 609.3 | 11.78 | 0.828 | 81.22 | 81.231
C4 | 5.2764e-10 |  | C4 | -2.5867e-11 |  | C4 | 4.912e-18 | 7000 | 2136 | 1 | 23.10 | 586.7 | 11.34 | 0.797 | 78.19 | 78.2205
C3 | 3.9016e-07 |  | C3 | 2.3912e-05 |  | C3 | -9.7201e-12 | 8000 | 2441 | -1 | 22.23 | 564.6 | 10.91 | 0.767 | 75.22 | 75.2982
C2 | 1.1203e-05 |  | C2 | -0.0065444 |  | C2 | 5.3618e-07 | 9000 | 2746 | -3 | 21.39 | 543.3 | 10.5 | 0.738 | 72.4 | 72.4624
C1 | 0.00047277 |  | C1 | 0.032332 |  | C1 | -0.011883 | 10000 | 3050 | -5 | 20.58 | 522.7 | 10.1 | 0.71 | 69.64 | 69.7205
b | 0.0060692 |  | b | 999.9926 |  | b | 101.2508 | 15000 | 4577 | -14 | 16.89 | 429.0 | 8.29 | 0.583 | 57.16 | 57.1678
[8 empty] | 20000 | 6102 | -24 | 13.76 | 349.5 | 6.76 | 0.475 | 46.61 | 46.5158
[8 empty] | 25000 | 7628 | -34 | 11.12 | 282.4 | 5.46 | 0.384 | 37.65 | 37.5454
[8 empty] | 30000 | 9153 | -44 | 8903 | 226.1 | 4.37 | 0.307 | 30.13 | 30.0789
[8 empty] | 35000 | 10679 | -54 | 7.06 | 179.3 | 3.47 | 0.244 | 23.93 | 23.9238
[8 empty] | 40000 | 12204 | -57 | 5558 | 141.2 | 2.73 | 0.192 | 18.82 | 18.9146
[8 empty] | 45000 | 13730 | -57 | 4375 | 111.1 | 2.15 | 0.151 | 14.82 | 14.8807
[8 empty] | 50000 | 15255 | -57 | 3444 | 87.5 | 1.69 | 0.119 | 11.65 | 11.6744
[8 empty] | 55000 | 16781 | -57 | 2712 | 68.9 | 1.33 | 0.0935 | 9.17 | 9.1503
[8 empty] | 60000 | 18306 | -57 | 2135 | 54.2 | 1.05 | 0.0738 | 7.24 | 7.1838
[8 empty] | 70000 | 21357 | -55 | 1325 | 33.7 | 0.651 | 0.651 | 4.49 | 4.4761
[8 empty] | 80000 | 24408 | -52 | 0.8273 | 21.0 | 0.406 | 0.406 | 2.8 | 2.8227
[8 empty] | 90000 | 27459 | -59 | 0.520 | 13.2 | 0.255 | 0.255 | 1.76 | 1.7607
[8 empty] | 100000 | 30510 | -46 | 0.329 | 8.36 | 0.162 | 0.162 | 1.12 | 1.1173

## Reference Tables
Barometric Pressure vs. Altitude
Altitude Above Sea Level |  | Atmospheric Pressure
Feet | Meters | PSI | Kg / cm2 | kPa
-5000 | -1526 | 17.48 | 1229 | 120.5
-4500 | -1373 | 17.19 | 1209 | 118.5
-4000 | -1220 | 16.9 | 1188 | 116.5
-3500 | -1068 | 16.62 | 1169 | 114.6
-3000 | -915 | 16.34 | 1149 | 112.7
-2500 | -763 | 16.06 | 1129 | 110.7
-2000 | -610 | 15.78 | 1109 | 108.8
-1500 | -458 | 15.51 | 1091 | 106.9
-1000 | -305 | 15.23 | 1071 | 105.0
-500 | -153 | 14.96 | 1052 | 103.1
0 | 0 | 14696 | 10333 | 101.33
500 | 153 | 14.43 | 1015 | 99.49
1000 | 305 | 14.16 | 0.996 | 97.63
1500 | 458 | 13.91 | 0.978 | 95.91
2000 | 610 | 13.66 | 0.960 | 94.19
2500 | 763 | 13.41 | 0.943 | 92.46
3000 | 915 | 13.17 | 0.926 | 90.81
3500 | 1068 | 12.93 | 0.909 | 89.15
4000 | 1220 | 12.69 | 0.892 | 87.49
4500 | 1373 | 12.46 | 0.876 | 85.91
5000 | 1526 | 12.23 | 0.86 | 84.33
6000 | 1831 | 11.78 | 0.828 | 81.22
7000 | 2136 | 11.34 | 0.797 | 78.19
8000 | 2441 | 10.91 | 0.767 | 75.22
9000 | 2746 | 10.5 | 0.738 | 72.40
10000 | 3050 | 10.1 | 0.71 | 69.64
15000 | 4577 | 8.29 | 0.583 | 57.16
20000 | 6102 | 6.76 | 0.475 | 46.61
25000 | 7628 | 5.46 | 0.384 | 37.65
30000 | 9153 | 4.37 | 0.307 | 30.13
35000 | 10679 | 3.47 | 0.244 | 23.93
40000 | 12204 | 2.73 | 0.192 | 18.82
45000 | 13730 | 2.15 | 0.151 | 14.82
50000 | 15255 | 1.69 | 0.119 | 11.65
55000 | 16781 | 1.33 | 0.0935 | 9.17
60000 | 18306 | 1.05 | 0.0738 | 7.24
70000 | 21357 | 0.651 | 0.651 | 4.49
80000 | 24408 | 0.406 | 0.406 | 2.80
90000 | 27459 | 0.255 | 0.255 | 1.76
100000 | 30510 | 0.162 | 0.162 | 1.12
Ref: www.engineeringtoolbox.com